# Schuylerville–Victory Board of Water Management

Meeting Minutes – November 17, 2025
Location: Village of Victory Hall
Time: 6:00 PM

## 1. Call to Order & Attendance

The meeting was called to order, and the Pledge of Allegiance was recited. Present: Chairman Drew, Commissioner Dennison, Commissioner Campbell, Commissioner Healy,

## 2. Board Announcements

- Next Water Board meeting: Monday, December 15, 2025 at 6:00 PM, Victory Hall.

## 3. Approval of Minutes

- Motion to approve October 2025 meeting minutes: Commissioner Dennison made the motion,  motion seconded by Commissioner Campbell

## 4. Treasurer’s Report

Balances as reported:

- Operating Account: $230,773.36

- NYCLASS Operating: $105,210.77

- Filter Account: $0

- NYCLASS Filter Account: $225,621.58

- Capital Reserve Savings: $0

- NYCLASS Capital: $64,748.13

## 5. JCF Plant Operator Report

### Schuylerville Plant

- Plant operating normally.

- October flow total: 5,514,640 gallons.

- Auto flusher at County Route 113 fixed with a new controller; adjusted for winter cycling.

### RO System (Reverse Osmosis)

- Both RO units underwent biannual CIPs the week of Nov 10; significant debris removed; membranes operating effectively.

- A cracked permeate port end cap on RO2 was replaced.

- Hypersperse chemical supply issue:

  - Longstanding supplier (OCS) lost access to the product.

  - Temporary alternative antiscalant obtained—more costly.

  - Current inventory: ~100-day supply.

  - JCF is contacting alternate vendors; will present quotes at next meeting.

  - Board to be notified immediately if lead times become problematic.

### Generator Service

- All three generators were fully serviced; no deficiencies.

- Water tower generator battery replaced.

### Ross Valve

- Internal gasket failure causing ongoing water loss.

- Ross Valve technician scheduled for Nov 20, 2025 to assess and repair.

### FCC Radio License

- Renewal required for communications between plants and tower.

- FCC website offline due to federal shutdown; JCF will renew once system is back online.

### Victory Plant

- October flow: 3,264,841 gallons.

- Operating without issues.

- Air scour blower piping reconfiguration ongoing.

## 6. Old Business

### 6.1 Auditor Update

- Cory Heyman Schuylerville Treasurer has contacted an additional auditing firm; awaiting a response.

### 6.2 Bank Signatory Resolution

- Resolution passed to add Jamie Porter (Schuylerville Clerk) and Tiffany Sini (Victory Deputy Clerk) to all Water Board accounts as authorized signatories.

- Chairman Drew made the motion Seconded by Commissioner Healy

### 6.3 Account Closures

- Filter Account and Capital Reserve Savings Account at Arrow Bank officially closed.

## 7. New Business

### 7.1 Hydrant Flushing

- Hydrant flushing complete in both villages.

- One hydrant requiring replacement:

  - 29 Burgoyne Street (Victory) — old DD hydrant not draining.

  - DPW to drain hydrant for winter; full replacement planned for spring 2026.

### 7.2 Property at 98 Green Street

- Possible two-family use; Board to request Code Enforcement to inspect for:

  - Additional meter(s)

  - Second kitchen (determining factor for classification)

### 7.3 Water Operator Licensing & Training

- January class on line-locating available ($250/person).

- Staff attending may include Rob, Jimmy, Tyler, Allen, Cayden.

- Weather may impact attendance—Board asked for confirmation of refund policy.

- Tyler must resolve missing high school diploma documentation to qualify for license.

### 7.4 Victory Plant Fence & Gate Issues

- Fence top rail damaged by mower; gate difficult to operate.

- Commissioner Drew to contact Anvil Fence regarding PM service and repairs for both Victory and Schuylerville gates.

### 7.5 Turbidimeter Calibration

- Quote from GCS for $1,590 for calibration.

- Commissioner Dennison made the motion and Chairman Drew Seconded the motion

### 7.6 Chlorine Reagent Purchase

- USA Blue Book quote: $1,476.62 for two cases (one year supply).

- Commissioner Dennison made the motion and Chairman Drew Seconded the motion

### 7.7 Grove Street Water Issue

- Ongoing intermittent wet spot under review; potential leak unclear.

- Commissioner Drew will contact Morris Coolidge for further investigation.

### 7.8 Gate Avenue Valve Boxes

- Two valve boxes at 110 & 112 Gates Ave need replacement.

- Work postponed to spring 2026 due to winter conditions.

## 8. Public Comment

- None.

### 9. Executive Session Clerk Compensation Change

- Jamie Porter requested moving from hourly pay to monthly stipend

- Commissioner Campbell made the motion and Commissioner Healy seconded the motion

## 10. Vouchers

- Motion to approve vouchers totaling $15,310.92: Approved unanimously. Commissioner Healy made the motion and motion Seconded by Commissioner Campbell

## 11. Adjournment

- Motion to adjourn meeting: Commissioner Dennison made the motion and motion Seconded by Chairman Drew

Respectfully submitted,
Jamie Porter
Recording Secretary, Schuylerville-Victory Board of Water Management